Welding & Hotwork Operations Safe Work Practices Checklist

University of Idaho

*****************************************************************************************************************

Welding and other hotwork should be performed in designated maintenance areas where appropriate controls are present whenever possible.

*****************************************************************************************************************

Conditions should allow all items on this list to be checked AYes@ before welding or other hotwork operations are permitted to proceed.

Yes           No	Welders, assistants and observers have been supplied with and instructed to wear appropriate eye, face, hearing and hand protection.

Yes           No	Welders and other persons in the work area will wear clothing that protects all parts of the body from burns and damage associated with the ultraviolet radiation produced.

Yes           No	If welding is performed overhead welders will wear leather caps or helmets and shoulder covers.

Yes           No	Welders will wear boots or similar substantial foot gear that completely covers the feet and ankles with pants-cuffs worn on the outside.

Yes           No	If work will be done on an elevated surface an effective means of fall protection is provided.

Yes           No	If work must be performed under wet/damp conditions, mats, platforms or other means are provided that effectively insulate workers from shock hazards.

Yes           No	Workers have been provided and have reviewed appropriate Material Data Safety Sheets for all potentially hazardous materials that will be used.

Yes           No	If compressed gas cylinders are present, they are secured in an upright position and caps are in place when not in use.

Yes           No	Mechanical ventilation is provided to pull welding fumes away from the welder and discharge exhaust fumes safely for welding that must be performed in an area where natural ventilation is not sufficient to maintain a safe atmosphere.

Yes           No	If hotwork will be performed in a confined space, continuous air monitoring will be performed and documented as required by the university=s confined space standard.

Yes           No	If hotwork will be performed in a confined space, compressed gas cylinders will remain outside the space and torches will be removed from space when not in use.

Yes           No	Appropriate respirators are provided and will be used if natural or mechanical ventilation is not sufficient for maintaining a safe atmosphere.  (NOTE:  Welding or cutting operations that involve materials containing fluorine compounds, stainless steel, zinc, lead, beryllium, cadmium, and mercury are especially hazardous and may require the use of both local ventilation and respiratory equipment to ensure adequate protection)

Yes           No	Gas welding hoses are equipped with flashback arrestors.

Yes           No	Noncombustible or flameproof flash screens are placed as needed to protect other personnel from flash and sparks.

Yes           No	Screens are positioned approximately 2 feet above the floor to allow for maximum ventilation (unless work must be performed at so low a level that they must be extended to the floor to provide protection).

Yes           No	The person(s) who will be performing hotwork are adequately trained and qualified.

Yes           No	Sprinklers located in the area where the hotwork will be performed are operational.

Yes           No	If smoke detectors are present and must be covered/de-activated to prevent false alarms, Environmental Health & Safety has been notified.

Yes           No	Cutting and welding equipment is in good repair.

Yes           No	Ducts and conveyor systems (that might carry sparks to distant combustibles) are suitably protected or shut-down.

Yes           No	Floors have been swept and cleared of all combustibles within 35 feet of hotwork (if possible).

Yes           No	Combustible floor or wall surfaces within 35 feet of hotwork are wet down or protected with damp sand, metal or other safety shields.

Yes           No	There are no unprotected combustible materials or flammable liquids in the hotwork area.

Yes           No	All combustibles that are likely to be ignited by conduction or radiation are moved away from the opposite side of partitions, walls, ceilings or roofs.

Yes           No	All wall and floor openings are covered.

Yes           No	Covers that need to be suspended beneath the work to collect sparks are installed.

Yes           No	All combustibles are cleaned and removed from equipment near the hotwork area.

Yes           No	Containers on which hotwork will be performed are purged of all flammable vapors.

Yes           No	Provisions have been made to provide a fire-watch during hotwork operations and for at least 30 minutes after the work is completed.

Yes           No	The fire watch is supplied with suitable fire extinguisher and other appropriate fire-suppression materials.

Yes           No	The fire watch is trained in the proper use of suppression equipment and how to sound the alarm if necessary.

Yes           No	Adjoining areas, above and below, have been checked for the necessity of fire watch.

Yes           No	An approved first-aid kit is readily available.

Yes           No	A phone with emergency numbers posted nearby is available and accessible.

OTHER:

Checklist Completed by:                                                               	Date:

Revised June 6, 2005